## COL (2)
Simple Cost of Light Analysis (SCOLA)
Prepared For:
Address:
Area Analized
Enter Data in Green Shaded Cells | Additional Information
Date:
Annual Operating hrs. |  | 1880 |  | Savings Calculation
Electricity cost (£ per kwh) |  | 0.11 |  | Savings over existing system | Alternate 1 | Alternate 2
[5 empty] | 150w led | 200w led
Lamp Information | Existing | Alternate 1 | Alternate 2 | Average Annual Savings | 3604.9376 | 3480.8576
Lamp designation | Fluorescent | 150w led | 200w led | Payback (years) | 2.9092 | 3.0205
No. of fixtures | 88 | 44 | 36 | Simple ROI | 34.37% | 33.11%
No. of lamps per fixture | 2 | 1 | 1 | Energy $ saved
Price per lamp (£) | 2.65 |  |  | PER FIXTURE over lamp life
Lamp rated life | 6000 |  |  | per year | 1728.848 | 1604.768
Spot relamping labor cost (£ per lamp) | 31.37
Ballast Information
Ballast description
No. of ballasts to be replaced
Price per ballast (£)
Input watts per fixture | 170 | 150 | 200
Labor cost to retrofit (per fixture) |  | 111.17 | 129.31
Investment Calculation
Total no. of lamps at site | 176 | 44 | 36
Total price of lamps |  | 0 | 0
Price of ballasts replaced | 0 | 0 | 0
Price of new fixture |  | 127.18 | 162.74
Total retrofit labor cost | 0 | 4891.48 | 4655.16
Investment to upgrade site | 0 | 10487.4 | 10513.8
Cost Calculation | Annual Operating Costs
Annual electricity costs | 3093.728 | 1364.88 | 1488.96 | Please Note: This Simple Cost of Light Analysis provides an estimate using "straight line" lamp mortality. It ignores impact on A/C systems, environmental savings, benefits of group relamping and quality of light considerations.
No. of lamps replaced annually | 55.1467 | 0 | 0
Annual cost of replacement lamps | 146.1387 | 0 | 0
Labor costs for relamping | 1729.9509 | 0 | 0
Annual cost of light (avg.) | 4969.8176 | 1364.88 | 1488.96
Note on B16: This calculation assumes that lamps are replaced as they fail.
Note on B15: Wherever possible, use the rated life corresponding to the number of hours per start.
Note on B21: For fluorescent fixtures use the ballast input watts as specified by the manufacturer; for HID lamps you could approximate to lamp watts +15% but it is best to get the actual number from the fixture or ballast manufacturer.
Note on B35: This assumes straight line mortality for lamps--a steady failure rate right from day one. In actuality there will be fewer failures in the first few years, so that payback is faster than what this model calculates.
Note on B22: In addition to labor,capture here anything other than lamp and ballast cost: incidentals like sockets, wiring etc.
Note on B23: "Differential costs" subtracts the cost of the existing lamp type and ballast when calculating the investment needed.
Note on B20: If the new lamps will operate on exising ballasts, no ballast change is needed. You may simply put 0 as the price of the ballast.

## Sheet1 (hidden)
| #REF! | #REF! | #REF!
Energy | #REF! | #REF! | #REF!
Labor | #REF! | #REF! | #REF!
Lamps | #REF! | #REF! | #REF!
Total | #REF! | #REF! | #REF!